## Sheet1
Consumption | Date | Plant 1 | Plant 2 | Plant 3 | Total
HFO-KL | 2024-04-02 |  | 0 |  | 0
HFO-KL | 2024-04-03 |  | 0 |  | 0
HFO-KL | 2024-04-04 |  | 1 / Unit hand tripped. |  | 1
HFO-KL | 2024-04-06 | 0 | 102.04 / UNIT LIGHTUP-UNIT SYN TO GRID AT 07.55 HRS |  | 102.04
HFO-KL | 2024-04-07 |  | 0 |  | 0
HFO-KL | 2024-04-08 |  |  | .93 / Oil consumed due to Mill C not available due to fire & Mill D Bunker Empty. | 0.93
HFO-KL | 2024-04-11 |  | 0 |  | 0
HFO-KL | 2024-04-13 |  | 24 / unit light up activities | 41.61 / Unit trip . again Lighted-up. | 65.61
HFO-KL | 2024-04-14 |  | 99.88 / unit light up | 39.22 / Unit start-up activity | 139.1
HFO-KL | 2024-04-15 |  | 0 |  | 0
HFO-KL | 2024-04-18 |  | 0 |  | 0
HFO-KL | 2024-04-19 |  | 0 |  | 0
HFO-KL | 2024-04-20 | 142.35 / unit light up activities |  |  | 142.35
HFO-KL | 2024-04-22 |  | 0 |  | 0
HFO-KL | 2024-04-23 |  | 0 | 3.62 / Unit Flame stabilization at drastic reduced load of 400MW | 3.62
HFO-KL | 2024-04-25 |  | 17.03 / ID FAN-2A - CH-2- Power cable inspection and testing work carried out. |  | 17.03
0
HFO-KL | 2024-04-26 |  | 0 |  | 0
HFO-KL | 2024-04-27 |  | 0 |  | 0
HFO-KL | 2024-04-30 | 0 | 0 | 4.14 / Mill Bunker ADF empty, so for flame stabilization and other bunker level low | 4.14
HFO-KL | 2024-05-01 | 0 | 0 | 3.33 / To maintain Flame stability due to Bunker D,E,F got empty and MRHS G chute got jam. | 3.33
HFO-KL | 2024-05-02
HFO-KL | 2024-05-04 |  | 0 |  | 0
HFO-KL | 2024-05-05 |  | 0 |  | 0
HFO-KL | 2024-05-08 | 0 | 0 |  | 0
HFO-KL | 2024-05-09 |  | 0 |  | 0
HFO-KL | 2024-05-12 |  | 0 | .28 / mill -A trip, low load | 0.28
HFO-KL | 2024-05-13 | 27.984 / Mill C under W/P, Mill E&F wet coal problem | 0 |  | 27.984
HFO-KL | 2024-05-16 |  | 0 |  | 0
HFO-KL | 2024-05-17 | 83.49 / unit lightup | 0 |  | 83.49
HFO-KL | 2024-05-18 |  |  | 72.57 / Boiler light up | 72.57
HFO-KL | 2024-05-19 | .5 / Ignition permit requirement |  | 88.66 / Boiler light up | 89.16
HFO-KL | 2024-05-20 |  | 0 |  | 0
HFO-KL | 2024-05-21 |  | 30.78 / Oil elevation taken @ 2.00 hrs since Specific coal consumption was 1.15kg/kwhr and taken out @09.30 |  | 30.78
HFO-KL | 2024-05-24 |  | 0 |  | 0
HFO-KL | 2024-05-25 | 0 | 0 |  | 0
HFO-KL | 2024-05-28 |  | 0 | 146.78 / boiler lightup activites | 146.78
HFO-KL | 2024-05-29 | 15.45 / ST-1 flash over | 0 |  | 15.45
HFO-KL | 2024-06-01 |  | 0 |  | 0
HFO-KL | 2024-06-02 |  | 0 |  | 0
HFO-KL | 2024-06-03 | 41.3 / Unit light up activities |  |  | 41.3
HFO-KL | 2024-06-05 |  | 0 | 129.03 / LIGHT UP ACTIVITY | 129.03
HFO-KL | 2024-06-06 |  | 0 |  | 0
HFO-KL | 2024-06-08 |  |  | 4.432 / For flame stability because of tripping of mills due to wet coal | 4.432
HFO-KL | 2024-06-09 | 0 | 0 | 2.76 / Ignition permit. wet coal | 2.76
HFO-KL | 2024-06-10 | .3774 / AB ELEVATION PTW , FLAME TEST | 0 | 13.58 / Feeder belt cut/stone stuck and ignition permit for mills | 13.9574
HFO-KL | 2024-06-11 | .166 / Trial Run |  | 1.58 / For Mill A Ignition permit | 1.746
HFO-KL | 2024-06-12 | .3 / Trial Run |  | 50.71 / For Light Up activities. | 51.01
HFO-KL | 2024-06-13 |  | 0 | 29.82 / Unit lightup activities | 29.82
HFO-KL | 2024-06-14 |  | 0 |  | 0
HFO-KL | 2024-06-17 | 0 | 0 | .36 / Flame stabilization | 0.36
HFO-KL | 2024-06-18 | 0 | 0 |  | 0
HFO-KL | 2024-06-19 | 6.8 / OBX Board tripped on Earth Fault |  |  | 6.8
HFO-KL | 2024-06-21 |  | 0 |  | 0
HFO-KL | 2024-06-22 |  | 0 |  | 0
HFO-KL | 2024-06-23 |  |  | 2.07 / Mill A ignition permit | 2.07
HFO-KL | 2024-06-24 |  |  | 1.03 / Mill A ignition permit | 1.03
HFO-KL | 2024-06-25 | 0 | 0 |  | 0
HFO-KL | 2024-06-26 | 0 | 0 |  | 0
HFO-KL | 2024-06-27 | 78.95 / Unit lit up |  |  | 78.95
HFO-KL | 2024-06-28 | 2.26 / HT board c/o |  |  | 2.26
HFO-KL | 2024-06-29 |  | 0 |  | 0
HFO-KL | 2024-06-30 |  | 0 | 121.88 / Light up | 121.88
HFO-KL | 2024-07-03 | 0 | 0 | 24.09 / Flame stabilization due to bunkers B C F empty and wet coal in other bunkers | 24.09
HFO-KL | 2024-07-04 |  | 10.14 / bunker feeding/wet coal | 110.38 / Flame stabilization, elecvation support, Bunker ABC F empty, CHP coal feeding problem. | 120.52
HFO-KL | 2024-07-05 |  |  | 49.34 / Bunker empty & wet coal | 49.34
HFO-KL | 2024-07-06 |  | 53.584 / PQC, PAF-B W/p |  | 53.584
HFO-KL | 2024-07-07 |  | 8.26 / Poor Quality coal . Higher specific coal consumption for that particular period >1.15 | 2.54 / for Stability of unit | 10.8
HFO-KL | 2024-07-08 |  | 17.4 / PAF-B problem |  | 17.4
HFO-KL | 2024-07-09 |  | 50 / P A fan-2B not available |  | 50
HFO-KL | 2024-07-10 |  | 30 / PA fan -2B not avilable |  | 30
HFO-KL | 2024-07-11 | 0 | 0 | 9.63 / Flame stabilization due to B E Bunker empty and Mill-C & F we coal | 9.63
HFO-KL | 2024-07-12 | 0 | 8.14 / FLAME STABILITY | 42.73 / Flame stabilization due freeqent Feeder unloading due to wet coal, Bunker Empty,etc,. | 50.87
HFO-KL | 2024-07-13 |  |  | 2.76 / Wet coal and Bunker Level Problem. | 2.76
HFO-KL | 2024-07-14 |  |  | .43 / For Flame stability | 0.43
HFO-KL | 2024-07-15 |  | 0 |  | 0
HFO-KL | 2024-07-16 |  | 0 |  | 0
HFO-KL | 2024-07-17 | 13 / MILL BUNKERS C & D EMPTY |  | 69.74 / Mill bunkers A,B,C,E,F empty | 82.74
HFO-KL | 2024-07-18 |  | 20.39 / Mills B,C and D not avialble | 9.84 / For flame stability since Mills C, D, G were not available | 30.23
HFO-KL | 2024-07-19 | 2.2 / mill suport | 44.24 / BUNKER JAM DUE TO WET COAL/ FLAME SUPPORT |  | 46.44
HFO-KL | 2024-07-20 |  | 0 |  | 0
HFO-KL | 2024-07-21 |  |  | 3.22 | 3.22
HFO-KL | 2024-07-22 |  |  | 42.9 / Bunker empty and for Flame stability | 42.9
HFO-KL | 2024-07-23 |  | 0 | 126.26 / bunker feeding problem | 126.26
HFO-KL | 2024-07-24 |  | 0 | 42.24 / Coal feeding problem | 42.24
HFO-KL | 2024-07-25 | 4.86 / Mill-A,E wet coal |  | 145.8 / Mill bunker levels low/empty | 150.66
HFO-KL | 2024-07-26 |  |  | 115.24 / Mill bunker C empty; Mill D & G wet coal. | 115.24
HFO-KL | 2024-07-27 |  | 0 | 49.38 / Flame stabilization due to freequent unloading of feeders due to wet coal and empty of bunkers | 49.38
HFO-KL | 2024-07-28 |  | 0 | 161.38 / Flame stabilization due to freequent unloading of mills by wet coal or bunker empty | 161.38
HFO-KL | 2024-07-29 |  |  | 4.66 / Wet coal | 4.66
HFO-KL | 2024-07-30 |  |  | 20.45 / Wet coal | 20.45
HFO-KL | 2024-07-31 |  | 0 | 34 / Flame stability due to low load,wet coal | 34
HFO-KL | 2024-08-01 |  | 0 | 9.55 / flame stability due to low load and wet coal. | 9.55
HFO-KL | 2024-08-02 |  |  | 7.96 / For flame stablity due to wet coal/bunker empty | 7.96
HFO-KL | 2024-08-03 |  |  | 68.73 / For flame stability due to wet coal/bunker empty | 68.73
HFO-KL | 2024-08-04 | 0 | 0 | 36.8 / Flame stability, Freequent unloading of feeders due to wet coal, bunker empty | 36.8
HFO-KL | 2024-08-05 | 0 | 0 | 34.39 / Flame stability, Freequent unloading of feeders due to bunker empty/wet coal | 34.39
HFO-KL | 2024-08-06 | .63 / bunker empty |  | 35 / BUNKER EMPTY | 35.63
HFO-KL | 2024-08-07 |  | 5 / Wet coal | 20 / Bunker Empty | 25
HFO-KL | 2024-08-08 |  | 3.334 / Flame Instability due to Higher Specific coal consumption. | 49.748 / FOR FLAME STABILITY DUE TO COAL PROBLEM | 53.082
HFO-KL | 2024-08-09 |  | 0 | 3.81 / To maintain flame stability | 3.81
HFO-KL | 2024-08-10 | .543 / Unit AOH, Bunkers empty |  |  | 0.543
HFO-KL | 2024-08-11 |  | 0 | 52.6 / Unit lightup activity | 52.6
HFO-KL | 2024-08-12 |  | 1.25 / For stabalization of ID Fans. | 90.77 / Unit Start-up activity | 92.02
HFO-KL | 2024-08-13 |  | 0 | 65.88 / Flame stabilization due to freequent feeder unload due to wet coal and bunke chockage, bunker empty | 65.88
HFO-KL | 2024-08-14 |  |  | 30 / Bunker Empty. | 30
HFO-KL | 2024-08-16 |  | 0 | 5.86 / flame stability | 5.86
HFO-KL | 2024-08-17 |  | 0 |  | 0
HFO-KL | 2024-08-18 |  | 35.78 / 2CB Board tripped | 17.03 / Flame stability | 52.81
HFO-KL | 2024-08-19 |  | 7.031 / Mills A,B and C not avilable | 173.46 / Flame stablility | 180.491
HFO-KL | 2024-08-20 | 0 | 0 | 121.55 / Flame stabilization due to freequent Bunker Empty, wet coal and coal feeding problem to bunkers | 121.55
HFO-KL | 2024-08-21 |  | 66.9 / Consumed for Unit light up activity | 82.99 / Flame stabilizaton due to freequent bunker empty,wet coal or foriegn material, CHP coal feed path | 149.89
HFO-KL | 2024-08-22 |  | 6.52 / Consumed for Unit lit up activity |  | 6.52
HFO-KL | 2024-08-24 |  | 0 |  | 0
HFO-KL | 2024-08-25 |  | 0 |  | 0
HFO-KL | 2024-08-28 |  | 0 |  | 0
HFO-KL | 2024-08-29 |  | 0 | 25.813 / Flame stabilization due to freequent unloading of Feeders due wet coal | 25.813
HFO-KL | 2024-08-30 |  |  | 46.25 / Wet coal | 46.25
HFO-KL | 2024-08-31 |  |  | 1.94 / For Mill Ignition Permit | 1.94
HFO-KL | 2024-09-01 |  | 0 | 1.22 / FLAME STABILITY | 1.22
HFO-KL | 2024-09-02 |  | 44.029 / Mills A,B,F,G not available. | 12.95 / for flame stability due to wet coal. | 56.979
HFO-KL | 2024-09-03 |  |  | 29.98 / Ignition permit & flame stability | 29.98
HFO-KL | 2024-09-04 |  |  | 2.72 / Ignition permit & Flame stability | 2.72
HFO-KL | 2024-09-05 |  | 10.18 / For Wet coal and Flame stability | 92.42 / Flame stablization: freequent unloading of feeders due to wet coal/bunker empty/coal feeding etc,. | 102.6
HFO-KL | 2024-09-06 |  | 35.856 / wet coal/ flame stabiltiy |  | 35.856
HFO-KL | 2024-09-07 |  |  | 50 / For Flame stability | 50
HFO-KL | 2024-09-08 |  |  | 50 / For Flame stability | 50
HFO-KL | 2024-09-09 |  | 137 / Unit Light up and synchronisation. |  | 137
HFO-KL | 2024-09-10 |  | 0 |  | 0
HFO-KL | 2024-09-12 |  |  | 176.91 / Unit Light up activities | 176.91
HFO-KL | 2024-09-13 |  | 0 | 6.11 / Flame stability | 6.11
HFO-KL | 2024-09-14 |  | 0 | .27 / During Scavenging of BC elevation, command taken by HONV and after a while closed the valve | 0.27
HFO-KL | 2024-09-17 |  | 0 |  | 0
HFO-KL | 2024-09-18 |  | 0 |  | 0
HFO-KL | 2024-09-20 |  |  | 69.34 / Unit light up activities | 69.34
HFO-KL | 2024-09-21 |  | 0 | 91.05 / Unit Start-up activity | 91.05
HFO-KL | 2024-09-22 |  | 0 |  | 0
HFO-KL | 2024-09-23 | 100 / Unit-1 Light up activites |  |  | 100
HFO-KL | 2024-09-24 | 168.6 / Unit-1 Light up activities |  |  | 168.6
HFO-KL | 2024-09-25 |  | 0 |  | 0
HFO-KL | 2024-09-26 |  | 0 |  | 0
HFO-KL | 2024-09-29 | 4.99 / Unit safe shut down,after hand tripping the unit. | 0 | 3.65 / Flame stabilization due to Mill-C&D feeder unloaded due to wet coal, Mill-G under PTW | 8.64
HFO-KL | 2024-09-30 |  | 0 | 80.21 / Flame stabilization as Mills-A/B/C/D are freequent unloaded due to wet coal, Mill-G under PTW | 80.21
HFO-KL | 2024-10-01 | 116 / Unit light up activities | 3 / 2CB board trip |  | 119
HFO-KL | 2024-10-02 | 112.52 / Unit Light up activities |  |  | 112.52
HFO-KL | 2024-10-03 | 9.4 / To changeover UT | 94.53 / Unit2 Light Up and synchronised and Load rised. | 16.97 / flame stability | 120.9
HFO-KL | 2024-10-04 |  | 0 | .18 / To support mills | 0.18
HFO-KL | 2024-10-05 | 0 |  | 24.95 / Ignition permit & flame stability | 24.95
HFO-KL | 2024-10-06 | 0 |  | 21.92 / Ignition permit & flame stability | 21.92
HFO-KL | 2024-10-07 |  | 0 |  | 0
HFO-KL | 2024-10-08 |  | 0 |  | 0
HFO-KL | 2024-10-11 |  | 0 |  | 0
HFO-KL | 2024-10-12 |  | 0 |  | 0
HFO-KL | 2024-10-15 | .8 / Safe shutdown | 0 |  | 0.8
HFO-KL | 2024-10-16 |  | 0 | 3.78 / Flame stabilization, Mills in service ABEG | 3.78
HFO-KL | 2024-10-17 | 67.48 / Unit LightUp |  | 69.04 / For Flame stability | 136.52
HFO-KL | 2024-10-18 |  |  | 179.09 / For Light up Activities. | 179.09
HFO-KL | 2024-10-19 | 5.2 / PQC and low flame intensity | 7.3 / Mill F and G Unloaded and For flame stability due to Poor quality coal. | 31.78 / . | 44.28
HFO-KL | 2024-10-20 |  | 0 | 53.28 / Wet coal. For Flame stability | 53.28
HFO-KL | 2024-10-21 |  |  | 2.06 / Flame stability | 2.06
HFO-KL | 2024-10-22 |  |  | 30.13 / Flame stability | 30.13
HFO-KL | 2024-10-23 | 0 | 0 | 87.69 / Flame stability due to wet coal, bunker empty, Mill/feeder un avilability | 87.69
HFO-KL | 2024-10-24 | 0 | 0 |  | 0
HFO-KL | 2024-10-26 |  |  | 5.39 / Flame stability | 5.39
HFO-KL | 2024-10-27 |  | 0 |  | 0
HFO-KL | 2024-10-28 |  | 0 |  | 0
HFO-KL | 2024-10-30 |  |  | 80.8 / Flame Stability | 80.8
HFO-KL | 2024-10-31 | 0 | 0 | 35 / flame stabilization due to Wet coal, stone stuck in feeders | 35
HFO-KL | 2024-11-01 |  | 0 | 33.1 / Flame stability due to freequent unloading of mill feeders due to wet coal and stones | 33.1
HFO-KL | 2024-11-02 |  |  | 21.82 / For Flame stability | 21.82
HFO-KL | 2024-11-03 |  |  | 5 / For Flame stability | 5
HFO-KL | 2024-11-04 | 4.74 / Mill - B not available and PQC | 0 |  | 4.74
HFO-KL | 2024-11-05 | 7.58 / PQC | 5.16 / Load raised with Oil elevation upto 350MW due to Higher SCC, inorder to check TDBFP-A vibrations. |  | 12.74
HFO-KL | 2024-11-06 |  |  | 1.76 / Flame Stability | 1.76
HFO-KL | 2024-11-07 | 7.94 / TDBFP-A TRIPPED,MDBFP NA | 8.77 / As per the request of EETM, took elevation &load raised for conducting vibration analysis of TDBFP-A | 9.28 / Flame stability | 25.99
HFO-KL | 2024-11-08 | 0 | 5.33 / For raising load up to 350MW for Correction of TDBFP-A's vibration by TM Staff (PTW No.19119) | 0.12 | 5.45
HFO-KL | 2024-11-09 | 0 | 0 | 29.3 / Flame stability due to coal feeding path not avilable | 29.3
HFO-KL | 2024-11-10 |  | 0 | 8.21 / For Flame stability | 8.21
HFO-KL | 2024-11-11 |  | 35.66 / IDF, FDF trip, |  | 35.66
HFO-KL | 2024-11-12 |  | 0 | 6.02 / mill A&C wet coal, mill E stone in feeder hence for maintain flame stability | 6.02
HFO-KL | 2024-11-13 |  | 0 | 3.61 / Oil elevation to avoid flame voting | 3.61
HFO-KL | 2024-11-15 |  |  | .84 / Flame stability | 0.84
HFO-KL | 2024-11-16 |  | 0 |  | 0
HFO-KL | 2024-11-17 |  | 0 |  | 0
HFO-KL | 2024-11-20 |  | 0 |  | 0
HFO-KL | 2024-11-21 |  | 0 | 103.47 / lightup activity | 103.47
HFO-KL | 2024-11-24 | 0 | 0 |  | 0
HFO-KL | 2024-11-25 | 0 | 0 |  | 0
HFO-KL | 2024-11-26 |  |  | .59 / For Flame stability | 0.59
HFO-KL | 2024-11-27 |  |  | 4.64 / For Flame stability | 4.64
HFO-KL | 2024-11-28 | 48.43 / Unit 1 light up activity | 0 | 2.81 / . | 51.24
HFO-KL | 2024-11-29 | 138.67 / Unit light up | 0 |  | 138.67
HFO-KL | 2024-11-30 | 2.55 / MILLS C&D UNLOADED |  |  | 2.55
HFO-KL | 2024-12-02 | 0 | 1.5 / Mill A permissive,whileB not available | 19.08 / MILLS B&D W/P | 20.58
HFO-KL | 2024-12-03 | 0 |  | 26.33 / Due to Wet Coal and Stones in feeders. | 26.33
HFO-KL | 2024-12-04 |  |  | 4.41 / For Flame stability | 4.41
HFO-KL | 2024-12-06 |  | 0 |  | 0
HFO-KL | 2024-12-07 |  | 0 |  | 0
HFO-KL | 2024-12-10 | 0 |  |  | 0
HFO-KL | 2024-12-11 | 0 | 0 | 136.5 / Unit Start-up activity | 136.5
HFO-KL | 2024-12-12 |  |  | .54 / Flame stability | 0.54
HFO-KL | 2024-12-14 | .66 / for flame stability due to non-availability of mills | 0 |  | 0.66
HFO-KL | 2024-12-15 |  | 0 |  | 0
HFO-KL | 2024-12-18 | 0 |  | 4.03 / Flame stability, freequent un-loading of feeders due to foreign materials wet coal and bunker empty. | 4.03
HFO-KL | 2024-12-19 | 0 |  | 0 | 0
HFO-KL | 2024-12-22 |  | 0 |  | 0
HFO-KL | 2024-12-23 |  | 0 |  | 0
HFO-KL | 2024-12-26 | 0 |  |  | 0
HFO-KL | 2024-12-27 | 0 |  |  | 0
HFO-KL | 2024-12-30 |  | 0 |  | 0
HFO-KL | 2024-12-31 |  | 0 |  | 0
HFO-KL | 2025-01-03 |  | 0 |  | 0
HFO-KL | 2025-01-04 |  | 0 |  | 0
HFO-KL | 2025-01-05 | 1.35 / Flame Stability |  |  | 1.35
HFO-KL | 2025-01-06 | 9.2 / Flame Stability |  |  | 9.2
HFO-KL | 2025-01-07 | 4.3 / MILLS D&G W/P & E,C&F FREQUENT FIRE | 0 |  | 4.3
HFO-KL | 2025-01-08 | 7.85 / Mills-A&G under W/P and fdr C, E unloaded | 0 |  | 7.85
HFO-KL | 2025-01-10 | 3 / MILLS-E,F UNLOADED MILL-G WP |  |  | 3
HFO-KL | 2025-01-11 |  | 0 |  | 0
HFO-KL | 2025-01-12 | 2.86 / ID fan A LOPs tripped,load reduced to 230MW | 0 |  | 2.86
HFO-KL | 2025-01-15 |  | 0 |  | 0
HFO-KL | 2025-01-16 |  |  | 190.1 / Unit light up activity | 190.1
HFO-KL | 2025-01-17 |  |  | 3.79 / Flame stability | 3.79
HFO-KL | 2025-01-19 |  | 0 |  | 0
HFO-KL | 2025-01-20 |  | 0 |  | 0
HFO-KL | 2025-01-23 |  | 0 | 81.88 / LIGHT UP ACTIVITY | 81.88
HFO-KL | 2025-01-24 | 1.396 / During unit shutdown activities | 0 |  | 1.396
HFO-KL | 2025-01-25 |  |  | 88.7 / unit light up | 88.7
HFO-KL | 2025-01-26 | 16.06 / UNIT LIGHTUP |  |  | 16.06
HFO-KL | 2025-01-27 | 76.94 / unit light up | 2.16 / Forflame support, mill problem |  | 79.1
HFO-KL | 2025-01-28 |  | 44.3 / FLAME SUPPORT FOR BUNKER EMPTY & UNIT HAND TRIP |  | 44.3
HFO-KL | 2025-01-29 | 3.16 / Flame Stability |  |  | 3.16
HFO-KL | 2025-01-30 | .66 / Flame Stability |  |  | 0.66
HFO-KL | 2025-02-04 | 0 |  |  | 0
HFO-KL | 2025-02-05 | 0 |  |  | 0
HFO-KL | 2025-02-12 | 0 |  | 0 | 0
HFO-KL | 2025-02-13 | 0 |  | 0 | 0
HFO-KL | 2025-02-14 |  |  | 117.04 / For light up activity | 117.04
HFO-KL | 2025-02-18 |  |  | 91.67 / Unit lightup activities | 91.67
HFO-KL | 2025-02-20 | 0 |  |  | 0
HFO-KL | 2025-02-21 | 0 |  |  | 0
HFO-KL | 2025-02-28 | 0 |  |  | 0
HFO-KL | 2025-03-01 | 0 | 142.94 / Unit light up | 0 | 142.94
HFO-KL | 2025-03-02 |  | 85.66 / Unit lit up and Start up | 0 | 85.66
HFO-KL | 2025-03-04 |  | 0 |  | 0
HFO-KL | 2025-03-05 |  | 0 |  | 0
HFO-KL | 2025-03-08 | 0 | 0 |  | 0
HFO-KL | 2025-03-09 | 0 | 0 |  | 0
HFO-KL | 2025-03-10 |  | 5.668 / Mill A, B F non available |  | 5.668
HFO-KL | 2025-03-11 |  | 2.63 / Due to non availability of Mill-A, C and E |  | 2.63
HFO-KL | 2025-03-12 |  | 0 |  | 0
HFO-KL | 2025-03-13 |  | 0 |  | 0
HFO-KL | 2025-03-16 | 0 | 0 |  | 0
HFO-KL | 2025-03-17 | 0 | 0 | 1.83 / for Unit Safe shutdown due to BTL | 1.83
HFO-KL | 2025-03-19 |  |  | 2.16 / For Light up activities | 2.16
HFO-KL | 2025-03-20 |  | 0 | 132.24 / Light up | 132.24
HFO-KL | 2025-03-21 |  | 0 |  | 0
HFO-KL | 2025-03-24 | 0 | 0 | 0 | 0
HFO-KL | 2025-03-25 | 0 | 0 | 0 | 0
HFO-KL | 2025-03-27 |  |  | 104.66 / For Light up activities | 104.66
HFO-KL | 2025-03-28 |  | 0 | 31.81 / after synchronisation and flame stability | 31.81
HFO-KL | 2025-03-29 |  | 0 |  | 0